ATTACHMENT A

Lease No: DTFA  -    - L -

I. SECTION A - GENERAL BUILDING REQUIREMENTS AND SPECIFICATIONS

A-1 Adhesives and Sealants (11/11)

The Lessor shall use adhesives and sealants that contain no formaldehyde or heavy metals.

A1-Ceilings (10/96)

Must have acoustical treatment with a flame spread of 25 or less and smoke development rating of 50 or less.

A2-Doors (10/96)

Exterior doors shall be weather tight, equipped with cylinder locks and door checks, automatic door closures and open outward. The FAA will be furnished at least two master keys and two keys for each lock. Interior doors must be solid cord and at least 32 by 80 inches with a minimum opening of 32 inches and be of sturdy construction. Fire doors shall conform to NFPA Standard No. 80. As designated by the FAA, doors shall be equipped with non-removable hinge pins, and "Best" locks with 7-pin removable cores. The FAA shall provide cores.

A3-Floor Load (8/02)

All adjoining floor areas shall be 1) of a common level not varying more than 1/4 inch over a 10-foot, 0-inch horizontal run in accordance with the American Concrete Institute standards, 2) non-slip, and 3) acceptable to the Real Estate Contracting Officer. Under floor surfaces shall be smooth and level. Office areas shall have a minimum live load capacity of 50 pounds per square foot plus 20 pounds per square foot for moveable partitions. Storage areas shall have a minimum live load capacity of 100 pounds per square foot including moveable partitions. A report showing the floor load capacity, at no cost to the Government, by a registered professional engineer may be required by the Contracting Officer.

A4-General Health and Safety Standards (8/02)

Local Health, Environmental (OSHA and EPA), and Safety Standards and Building Codes shall be complied with when accomplishing any cleaning, construction, renovation, remodeling, maintenance or testing done in the leased space and areas connected to or integrated with the leased space. Whenever FAA Standards require work processes or precautions to be provided, the Lessor shall coordinate with the FAA during the work so that proper requirements are met.

A5-HVAC (10/96)

Heating, ventilation and air-conditioning systems are required which maintain a temperature range of 68-72 degrees Fahrenheit year-round. These temperatures must be maintained throughout the leased premises and service areas regardless of outside temperatures during hours of operation. For further information see ASHRAE standard ANSI/ ANSI/ASHRAE 62-1999 - Ventilation for Acceptable Indoor Air Quality.

A6-Lighting (10/96)

Modern, diffused, energy efficient (T-8 or better) fluorescent fixtures shall be provided maintaining a uniform lighting level of 50 foot candles at working surfaces. Emergency lighting must provide at least 0.5 foot candles of illumination throughout the exit path, including exit access routes, exit stairways, or other routes such as passageways to the outside of the building.

A7-Painting (8/02)

Prior to occupancy all surfaces must be newly painted with non-lead based paints in colors acceptable to the FAA. All surfaces must be repainted after working hours at Lessor’s expense at least every five years. This includes moving and return of the furniture.

Any existing lead based paint shall be properly maintained and managed per existing regulatory requirements. If there is flaking paint, it would need to be sampled for lead. If containing lead, it would need to be abated prior to occupancy. This could be done either by removal or sealing with an encapsulating material.

A8-Parking (10/06)

At no additional cost to the FAA, the Lessor shall provide ** reserved off-street parking spaces located **. The Lessor shall maintain the parking areas in good repair and provide snow and ice removal.

A9- Prior Notification (8/02)

A pre-construction meeting shall be held at the facility prior to the commencement of any cleaning, construction, renovation, remodeling, repair, maintenance or testing within the leased premises and areas connected to or integrated with the leased premises. If any items on the checklist are questionable or undone, full resolution of the issues will be expected before the project starts. The pre-construction meeting will be planned, scheduled, and coordinated, with the Government’s supervisor or manager responsible for the facility, at least one week before the execution of the work.

A10-Restrooms and Drinking Fountains (7/09)

Separate toilet facilities for men and women shall be provided on each floor where the FAA leases space. Water closets and urinals shall not be visible when the exterior door is open. Each toilet room shall contain toilet paper dispensers, soap dispensers, paper towel dispensers, waste receptacles; a coin operated sanitary napkin dispenser with receptacle for each women's toilet, disposable toilet seat cover dispensers, a convenience outlet, and hot and cold water for all restrooms. (The FAA will advise if additional facilities are required.). The Lessor shall provide a minimum of one chilled accessible drinking fountain with potable water within every 200 feet of travel.

A11-Window and Floor Covering (8/02)

All exterior windows shall be equipped with window covering. Floors will be carpeted with a commercial grade of carpet acceptable to the FAA. Existing floor and window covering may be accepted at the discretion of the Real Estate Contracting Officer however; prior to occupancy all carpeting and window covering shall be cleaned.

At no additional cost to the FAA, the Lessor shall replace carpeting at least every eight (8) years during FAA occupancy or any time during the lease when:

- Backing or underlayment is exposed

- There are noticeable variations in surface color or texture

Replacement includes moving and return of furniture.

II. SECTION B - SERVICES, UTILITIES, AND MAINTENANCE

B1-Grounds Maintenance (10/96)

The Lessor shall maintain in good condition landscape plants and lawns. The Lessor shall also remove snow and ice from the entrances, exterior walks and parking areas around the premises, prior to and during the Government’s normal operating hours.

B2-Pest Control (8/02)

The Lessor shall exterminate and control pests within the premises within a timely manner as required by the Government. Notice shall be provided to the users of the building before any application of herbicide(s)/pesticide(s) or other chemical pest control. OSHA requirements for Hazard Communication shall apply for the use of hazardous materials used in pest control. Copies of Material Safety Data Sheets (MSDS) for all chemicals applied shall be provided to the FAA before application. Only licensed applicators shall be allowed to apply chemicals. Herbicides/pesticides are not to be applied near the outside air intakes of the building during normal working hours and when the system is in operation.

B3-Services and Facilities (10/96)

The Lessor shall provide to the Government, as part of the rental consideration, the following:

- Heating, air conditioning, and ventilation that provide for the comfortable occupancy of the premises. Temperatures will be thermostatically controlled to maintain a temperature of 68 - 72 degrees Fahrenheit. These temperatures must be maintained throughout the leased premises and service areas, regardless of outside temperatures, during the FAA's normal hours of operation.

- Electrical power to the premises for the operation of lights, communications equipment, and office machines.

- Water (hot and cold) and sewer to leased premises.

- Trash removal for leased premises.

B4-Utilities Not Provided By The Lessor (10/96)

If the cost of utilities is not included as part of the rental consideration, the Lessor must specify which utilities are excluded. The Lessor shall provide separate meters for utilities to be paid for by FAA. When FAA is to pay for utilities, the Lessor will furnish the Real Estate Contracting Officer, prior to occupancy by the FAA, written verification of the meter numbers and certification that these meters will measure FAA usage only. Proration is not permissible. If the cost of utilities for heating, ventilation, and air conditioning is not included as part of the rental considerations, an automatic control system will be provided to assure compliance with heating and air conditioning provisions included in this specifications package.

III. SECTION C - SAFETY AND FIRE PREVENTION

C1-Fire and Safety Requirements (8/02)

All NFPA Standards addressed in this section reference the current edition of NFPA in place at the signing of this contract. At any point when construction takes place, systems should be brought into compliance according to the current edition of NFPA. The building shall, as required by Code, be equipped with automatic sprinklers which conform to NFPA No. 13, be maintained in accordance with NFPA No. 13A, have electrically supervised control valves (NFPA No. 13), and have water-flow alarm switches connected to automatically notify the local fire department (NFPA No. 72) or central station (NFPA No. 71). The notification of the fire department or central station shall be accomplished through the building fire alarm system. Regardless of code requirements when the leased space (including garage areas under lease by the FAA) is on the 6th floor and above, or below grade, sprinklers are required.

A manual fire alarm system shall be provided, maintained, and tested by the Lessor in accordance with NFPA Standard No. 71 and 72 in buildings, which are three (3) or more stories in height or contain more than 50,000 square feet gross floor area. The fire alarm system wiring and equipment must be electrically supervised and automatically notify the local fire department and conform to NFPA Standards No. 70 and 72. Engineered smoke control systems, if present, shall be maintained in accordance with the manufacturer’s recommendations.

Fire-safety, equivalent to the requirements stated above in this clause, may be accepted, at the discretion of the Real Estate Contracting Officer, if certified by a Licensed Fire Protection Engineer.

Portable fire extinguishers shall be provided, inspected, and maintained by the Lessor in accordance with NFPA Standard No.10.

C2-Halon (8/02)

Wherever halon is used in a facility as a fire extinguishing system, the Lessor shall comply with all NFPA standards regarding use of and safety requirements for the use of halon.

C3-Indoor Air Quality (8/02)

The Lessor shall control contaminants at the source and/or operate the space in such a manner that the indicator levels for carbon monoxide (CO), carbon dioxide (CO2), and formaldehyde (HCHO), are not exceeded. The indicator levels for office area are as follows: CO-9 parts per million (PPM) time weighted average (TWA - 8-hour sample); CO2 - 1,000 PPM (TWA); HCHO - 0.1 PPM (TWA). All indoor air contaminant levels in leased space will be kept below appropriate OSHA regulations or Consensus standards, whichever is stricter. Air quality and facility cleaning will be adequate to prevent the growth of mold, mildew and bacteria. Any visual evidence of these will require immediate sampling and remediation. Moisture/standing water will be controlled to prevent the growth of these.

During working hours, ventilation shall be provided in accordance with the latest edition of ANSI/ASHRAE Standard 62, Ventilation for Acceptable Indoor Air Quality.

The Lessor shall promptly investigate indoor air quality (IAQ) complaints and shall implement controls including alteration of building operating procedures (e.g., adjusting air intakes, adjusting air distribution, cleaning and maintaining HVAC, etc.). The FAA is responsible for addressing IAQ problems resulting from its own activities.

MSDS will be provided for all cleaning solutions used in the FAA spaces.

C4-OSHA Requirements (10/96)

The Lessor shall provide space, services, equipment, and conditions that comply with Occupational Safety and Health Administration (OSHA) safety and Health standards (29 CFR 1910 and 1926).

C5-Radon (10/96)

Radon levels in space leased to the FAA shall not equal or exceed the EPA action level for buildings of four (4) picocuries per liter (pCi/L). If radon levels are found to be at or above 4 pCi/L, the Lessor shall develop and promptly implement a plan of corrective action.

C6-Refrigerants (8/02)

The Lessor shall identify which refrigerants are used in the HVAC systems in the spaces covered by this lease. The lease should provide for use of refrigerants consistent with EPA and ASHRAE requirements.

C7-Warranty Of Space (8/02)

(a) Notwithstanding inspection and acceptance by the Government or any provision concerning the conclusiveness thereof, the Lessor warrants that all space leased to the Government under this contract, spaces above suspended ceilings in the leased space, air plenums elsewhere in the building which service the leased space, engineering spaces in the same ventilation zone as the leased space, public spaces and common use space (e.g., lobbies, hallways) will, at the time of acceptance and during the term of the lease contract, comply with the asbestos containing material (ACM) and polychlorinated biphenyl (PCB) requirements of the Toxic Substance Control Act. The Real Estate Contracting Officer shall notify the Lessor in writing, within 30 days after the discovery, of any failure to comply with the asbestos requirement. With any construction work, Lessor would be required to comply with the OSHA regulations for Asbestos and relevant FAA orders.

(b) The leased premises shall be free of all asbestos-containing material, PCB’s, Radon, and other environmentally hazardous substances. If either ACMs or PCBs are found to be in the leased space the Government reserves the right to require the Lessor, at no cost to the GOVERNMENT, to take whatever corrective action as might be required by the Toxic Substance Control Act, EPA regulations and state requirements. All facilities constructed prior to 1981 are to have an asbestos building survey conducted by a qualified inspector including a visual examination and bulk sampling. All ACM survey reports are to be made available to the Real Estate Contracting Officer.

(c) If the Lessor fails, after receipt of notice, to make correction within the specified period of time, the Government shall have the right to make correction and charge to the Lessor the costs occasioned to the FAA or terminate the lease agreement at no cost to the Government.

(d) The rights and remedies of the FAA in this clause are in addition to any other rights and remedies provided by the law and under this contract.

(e) Definitions.

- (1) "Acceptance", as used in this clause means the act of an authorized representative of the Government by which the Government assumes for itself, or as an agent of another, the leased premises as ready for occupancy or approves a portion of the premises for occupancy in accordance with the provisions of this lease contract.

- (2) "Correction", as used in this clause, means (i) the removal, encapsulation or enclosure of any friable asbestos materials found in the space leased to the Government, spaces above suspended ceilings in the leased space, air plenums elsewhere in the building which service the leased space, public spaces, engineering spaces in the same ventilation zone as the leased space and common use space (e.g., lobbies, hallways). Following such abatement actions, the Lessor shall adhere to the FAA's required post-asbestos-abatement air monitoring program. (ii) With regard to non-friable asbestos materials in good condition, it means the establishment and execution of a special operations and maintenance program and an abatement plan, approved by the Government, to be implemented from the time the materials are discovered through the remainder of the lease term, and (iii) with regard to PCBs, it involves the removal or retrofitting, in accordance with EPA regulations, of any PCB equipment present in the building.

IV. SECTION D – MISCELLANEOUS

D1-Adjustment For Vacant Premises (10/96)

If the Government fails to occupy any portion of the leased premises or vacates the premises in whole or in part prior to expiration of the firm term of the lease, the rental rate shall be reduced as follows: The rate shall be reduced by that portion of the costs per square foot of operating expenses not required to maintain the space. Said reduction shall occur after the Government gives 30 days prior notice to the Lessor, and shall continue in effect until the Government occupies the premises or the lease expires or is terminated.

D2-Condition Report (10/96)

A joint physical survey and inspection report of the demised premises will be made as of the effective date of this lease, reflecting the then present condition, and will be signed on behalf of the parties hereto.

D3-Contracting Officer’s Representative (COR) (10/96)

The Lessor shall address all questions concerning this lease to <insert name of COR>who has been appointed the Contracting Officer's Representative for the administration of this lease, as written.

D4-Day to Day Extension (8/02)

The Government shall continue to occupy the premises for a period not to exceed 180 days after the end of the lease term including all option periods. The rent shall be paid monthly in arrears on a prorated basis at the rate paid on the date of the lease expiration, until one of the following events occurs: (1) the extension day period expires: (2) a new lease commences, (3) the Government acquires a fee simple or other long-term interest in the property through negotiation or eminent domain or (4) the Government vacates the leased premises; whichever occurs first. The accrued rent computed on a daily basis shall be due and payable in arrears at the end of each month until the amount accrued by the end of the month has been fully paid.

D5-Display Advertising (10/96)

If the leased premises are solely for Government use, no advertising matter shall be constructed on or over the premises, unless authorized by the Real Estate Contracting Officer.

D6-Erection of Signs (10/96)

The Government shall have the right to erect on or attach to the Lessor's premises such signs as may be required to clearly identify the Government's facility. Said signs so erected will remain the property of the Government and shall be removed from the premises upon termination of the Lease.

D7-Hold Harmless (10/96)

In accordance with and subject to the conditions, limitations and exceptions set forth in the Federal Tort Claims Act of 1948, as amended (28 USC 2671 et. seq.), hereafter termed "the Act" the Government will be liable to persons damaged by any personal injury, death or injury to or loss of property, which is caused by a negligent or wrongful act or omission of an employee of the Government while acting within the scope of his office or employment under circumstances where a private person would be liable in accordance with the law of the place where the act or omission occurred. The foregoing shall not be deemed to extend the Government's liability beyond that existing under the Act at the time of such act or omission or to preclude the Government from using any defense available in law or equity.

D8-If Minimum Not Delivered (10/96)

If delivered space contains less than the minimum square footage, the Government may cancel the lease. If such cancellation occurs, the Government may exercise it’s legal rights including charging the Lessor and its surety the increased cost of providing replacement space.

D9-Installation Of Antennas, Cables And Other Appurtenances (10/96)

The FAA shall have the right to install, operate and maintain antennas, wires and their supporting structures including any linking wires, connecting cables and conduits atop and within buildings and structures, or at other locations, as deemed necessary by the Government.

D10-Interest For Late Payments (10/96)

If requested from the Lessor, the Government will pay an interest penalty when payment is not made within (30, 45, 60, 90, etc.)<insert number of days> days of the due date.

Payment shall be considered as being made on the day a check is dated or an electronic funds transfer is made. All days referred to in this clause are calendar days, unless otherwise specified. Rent shall be paid monthly in arrears and will be due on the first workday of each month and only as provided for by the lease.

The interest penalty shall be at the rate established by the Secretary of the Treasury under Section 12 of the Contract Disputes Act of 1978 (41 U.S.C. 611) that is in effect on the day after the due date. This rate is referred to as the "Renegotiation Board Interest Rate," and it is published in the Federal Register semiannually on or about January 1 and July 1. Interest penalties of less than $1.00 need not be paid.

Interest penalties will not be paid on delays due to disagreement between the Government and Lessor over the payment amount, requests for additional information or other issues involving contract compliance or on amounts temporally withheld or retain in accordance with the terms of the contract.

Payments other than rent, the Lessor shall prepare and submit an invoice to the designated billing office after completion of the work. An invoice shall include the following items:

(i) Name and address of the Lessor.
(ii) Invoice date.
(iii) Lease Number
(iv) Government’s order number or other authorization.
(v) Description, price, and quantity of work or services delivered.
(vi) Name and address of Contractor official to whom payment is to be sent

D11-Janitorial Services (11/11)

The Lessor shall maintain the leased premises, including outside areas in a clean condition. The Lessor shall provide the labor, materials, equipment and supervision necessary to ensure such condition.  .  The Lessor shall provide janitorial services for the leased space, public areas, entrances, and all other common areas and shall provide replacement of supplies.

A.SELECTION OF CLEANING PRODUCTS:

The Lessor shall select, to the maximum extent practicable janitorial cleaning products and equipment that promote environmental stewardship.  At a minimum, the Lessor shall:

1. Use products that are packaged ecologically;

2. Use products and equipment considered environmentally beneficial and/or recycled products that are phosphate-free, non-corrosive, non-flammable, and fully biodegradable; and;

3. Minimize the use of harsh chemicals and the release of irritating fumes.

Examples of acceptable products may be found at www.gsa.gov/p2products.

B. SELECTION OF PAPER PRODUCTS:

The Lessor shall select paper and paper products (i.e., bathroom tissue and paper towels) with recycled content conforming to EPA’s Comprehensive Procurement Guidance (CPG).

C.SCHEDULE OF CLEANING:

Cleaning shall be performed after the close of the official business day as defined in this lease, unless cleaning during official duty hours is specified as a special requirement.  The required cleaning services, and their frequencies, are set forth below:

1. Daily:

a. Sweep floors using chemically treated absorbent or dusting tools (such as DEX or equal). 
b. Carpet sweep all carpeted areas, as needed.
c. Empty waste baskets and containers; dispose of waste paper, trash, and other extraneous materials.
d. Clean toilets rooms, including toilets and soap containers.  Furnish and maintain constant supply of deodorant material.
e. Wash all drinking fountains.

f. Refill hand sanitizer dispensers in common areas, where applicable
g. In the restrooms:

- Clean restroom fixtures and chrome fittings.

- Clean and refill all dispensers (including deodorant material).

- Wet mop restroom floors.

- Sanitize toilets, toilet seats, and urinals.

- Spot wash walls, partitions, and doors.

2. Weekly:

a. Dust counters, file cabinets, and telephones, and surfaces of all office furniture, fixtures, and window sills (except desk tops).
b. Damp mop, and buff all non-carpeted floors.
c. Vacuum all carpeted areas.

3. Monthly:

- Wash waste baskets.

- Damp mop and buff all non-carpeted floors; wax and buff non-carpeted floors.

- Clean or wash walls as needed to present a neat appearance.

- Dust all ledges and flat surfaces within reach.

- Dust and clean all light fixtures.

- Dust and clean all venetian blinds.

- Wash restroom walls, partitions, and doors.

4. Semi-Annually:

a. Wash all exterior office windows.
5. Once a Year:
a. Strip old wax from all floor space and rewax.  This service is to be performed in conjunction with one of the quarterly cleaning schedules.
b. Shampoo all carpeted floors.

Within 60 days after occupancy by the Government, the Lessor shall provide to the RECO with a detailed written schedule of all periodic services and maintenance to be performed other than daily, weekly, or monthly.

D12-Landscaping (11/11)

A. Where conditions permit, the site shall be landscaped for low maintenance and water conservation with plants that are either native or well-adapted to local growing conditions.

B. Landscape management practices shall prevent or minimize pollution by:

1. employing practices which avoid or minimize the need for fertilizers and pesticides;

2. prohibiting the use of the 2,4-Dichlorophenoxyacetic Acid (2,4-D) herbicide and organophosphates; and

3. composting/recycling all yard waste.

C. The Lessor shall use landscaping products with recycled content that meets the requirements as required by Environmental Protection Agency's (EPA's) Comprehensive Procurement Guidelines (CPG) for landscaping products. Refer to EPA's CPG web site, WWW.EPA.GOV/CPG.

D. The Contracting Officer shall approve the landscaping to be provided in writing.

D13-Measurement For Payment (10/96)

The space will be mutually measured upon delivery. Payment will be made on the basis of actual measurement; however, payment will not be made for delivered space, which is in excess of the maximum square footage solicited.

D14-Non-Restoration (10/96)

The FAA shall have no obligation to restore and/or rehabilitate, either wholly or partially, the premises under this lease. It is further agreed that the FAA may abandon in place any or all of the structures, improvements and/or equipment installed in or located upon said property by the FAA during its tenure. Notice of abandonment will be conveyed to the Lessor in writing.

D15–Occupancy Permit (8/02) - The premises offered shall have a valid Occupancy Permit, issued by the local jurisdiction, for the intended use of the Government, or the Offeror shall complete and provide a certified copy of "FAA Safety & Environmental Checklist” form, in lieu of an occupancy permit, at the contracting officer’s discretion. The leased premises, all accesses to the leased premises, building operations,    equipment, services, or utilities furnished by the Lessor, and activities of other occupants, shall be free of safety, health, and fire hazards. When such hazards are detected, they must be promptly corrected at the Lessor's expense.

D16-Operating Costs Escalator (10/96)

Beginning with the second year of the lease and each year after, Government shall pay adjusted rent for changes in costs for cleaning services, supplies, materials, maintenance, trash removal, landscaping, water, sewer charges, heating, electricity, and certain administrative expenses attributable to occupancy.

The amount shall be determined by multiplying the total first year's estimated costs of these items, as negotiated and established prior to the lease award, by the percent of change in the cost of living index from the base figure. The base figure shall be the index figure published for the month prior to the lease commencement date. The percent change shall be computed by comparing the base figure with the index figure published for the month, which begins each successive l2-month period. For example, a lease which commences in June of 1981 would have as the base figure the index published for May of 1981, and that figure would be compared with the index published for May of 1982, May of 1983, and so on, to determine the percent change. The U.S. Department of Labor Revised Consumer Price Index shall measure the cost of living index for Wage Earners and Clerical Workers, U.S. City Average, All Items figure, (1967=100) published by the Bureau of Labor Statistics. Payment shall be made with the monthly installment of fixed rent.

Rental adjustments shall be effective on the anniversary date of the lease. Payment of the adjusted rental rate shall become due on the first workday of the second month following the publication of the cost of living index for the month prior to the lease commencement date.

If Government exercises an option to extend the lease term at the same rate as that of the original term, the option price shall be based on the adjustments during the original term. Annual adjustments will continue.

In the event of any decreases in the cost of living index occurring during the term of occupancy under the lease, the rental amount will be reduced accordingly. The amount of any such reductions will be determined in the same manner as increases in rent provided under this clause.

The base for the operating costs adjustment will be $_<insert base amount for operating costs>

D17-Plans (8/02)

Thirty days after occupancy, Lessor must submit a final set of hard copy as-built plans and reproducible floor plans in l/8" scale depicting rented space and identifying entrances, exits, stairs, windows, partitions, closets, architectural, construction documents to include but not limited to electrical, mechanical, structural, fire protection, plumbing plans, architectural plans, lighting plans, furniture plans, installation plans, typical workstations, etc. A CAD program compatible with the latest release of AutoCAD and accessible and readable by the Government for future use shall generate the plans. The file(s) will be dwg format. All files shall be submitted on 3-1/2-inch double-sided, high-density diskettes, or, if approved by the Contracting Officer, on CD-ROM or QIC (1/4-inch cartridge) tape. The submitted disks shall be labeled with building name, address, list of drawing(s), date of the drawing(s), and Lessor's architect and phone number. The Lessor’s operators shall demonstrate the submission on FAA equipment, if requested by the Real Estate Contracting Officer.

D18-Progressive Occupancy (10/96)

The Government shall pay rent only when the entire premises or suitable units are ready for occupancy. If the agency occupies the space in partial increments, rent will accrue or be paid on a pro rata basis. Rental payments shall become due on the first workday of the month following the month in which an increment of space is occupied, except that should an increment of space be occupied after the fifteenth day of the month, the payment due date will be the first workday of the second month following the month in which it was occupied. The commencement date of the firm term will be a composite determined from all dates of incremental occupancy.

D19 – Recycling (11/11)

Where State or local law, code, or ordinance requires recycling programs (including those for mercury containing lamps) for the space to be provided, the Lessor shall comply with such State and/or local law, code, or ordinance, to the extent practicable, and provided that any such law, code, and/or ordinance is at least as stringent as the requirements set forth under Federal law and in the immediately following paragraph below.

In all other cases, the Lessor shall establish a recycling program for (at a minimum) paper, corrugated cardboard, glass, plastics, and metals where local markets for recovered materials exist. In addition, the Lessor shall provide an easily accessible, appropriately sized (2 square feet per 1,000 square feet of building gross floor area) area that serves the tenant space for the collection and storage of materials for recycling. Telecom rooms are not acceptable as recycling space. The Lessor agrees, upon request, to provide the Government with additional information concerning recycling programs maintained in the building and in the leased space after lease execution.

D-20 Recycled Content Products (Comprehensive Procurement Guidelines) (11/11)

A. To the extent feasible, the Lessor shall comply with the Resource Conservation and Recovery Act (RCRA), Section 6002, 1976. The Lessor shall use recycled content products as indicated in this SFO and in the resultant lease and as designated by the U.S. Environmental Protection Agency (EPA) in the Comprehensive Procurement Guidelines (CPG), 40 CFR Part 247, and its accompanying Recovered Materials Advisory Notice (RMAN). The CPG lists the designated recycled content products. EPA also provides recommended levels of recycled content for these products. The list of designated products, EPA's recommendations, and lists of manufacturers and suppliers of the products can be found at the www.epa.gov/cpg/products.htm web site.

B. The Lessor, if unable to comply with both the CPG and RMAN lists, shall submit a request for waiver for each non-compliant material to the RECO. The request for waiver shall be based on one of the following criteria: 1. the cost of the recommended product is unreasonable; 2. inadequate competition with respect to product manufacturers exists; 3. compliant items are not available within a reasonable period of time; and 4. items do not meet the requirements of Attachment A to this Lease.

D-20-Tax Adjustment (10/96)

(a) The Government shall pay additional rent for its share of increases in real estate taxes over taxes paid for the calendar year in which its lease commences (base year). Payment will be in a lump sum and become due on the first workday of the month following the month in which paid tax receipts for the base year and the current year are presented, or the anniversary date of the lease, whichever is later. The Government will be responsible for payment only if the receipts are submitted within 60 calendar days of the date the tax payment is due. If no full tax assessment is made during the calendar year in which the Government lease commences, the base year will be the year of a full assessment.

(b) The Government's share of the tax increase will be based on the ratio of the square feet occupied by the Government to the total rentable square feet in the building. If the Government's lease terminates before the end of a calendar year, payment will be based on the percentage of the year in which the Government occupied space. The payment will not include penalties for non-payment or delay in payment. If there is any variance between the assessed value of the Government's space and other space in the building, the Government may adjust the basis for determining its share of the tax increase.

(c) The Government may contest the tax assessment by initiating legal proceedings on behalf of the Government and the Lessor or the Government alone. If the Government is precluded from taking legal action, the Lessor shall contest the assessment upon reasonable notice by the Government. The Government shall reimburse the Lessor for all costs and shall execute all documents required for the legal proceedings. The Lessor shall agree with the accuracy of the documents. The Government shall receive its share of any tax refund. If the Government elects to contest the tax assessment, payment of the rent shall become due on the first workday of the month following conclusion of the appeal proceedings.

(d) In the event of any decreases in real estate taxes occurring during the term of occupancy under the lease, the rental amount will be reduced accordingly. The amount of any such reductions will be determined in the same manner as increases in rent provided under this clause.

D21-Time Extensions (10/96)

The lease will not be terminated nor the Lessor charged with resulting damage if delays arise from unforeseeable causes beyond the control of the Lessor and/or his contractors, subcontractors, suppliers, or another Government contractor. However, the Lessor shall notify the Real Estate Contracting Officer, in writing, of any delay within 10 calendar days after it begins. The Real Estate Contracting Officer shall ascertain the facts, determine the extent of the delay, and grant extensions when justified.

D22-Unauthorized Negotiating (10/96)

In no event shall the Lessor enter into negotiations concerning the space leased or to be leased with other than the real estate contracting officer or his designee.

D23-Wiring For Telephones (10/96)

The Government reserves the right to provide its own telephone service in the space to be leased. It may have inside wiring and telephone equipment installed by the local telephone company or a private contractor. Alternately, the FAA may wish to consider using inside wiring provided by the building, if available. However, the final decision will remain the Government.

SECURITY REQUIREMENTS

E1-Facility Security  (Updated 4/09)

Security requirements for Government occupied space must meet minimum-security accreditation standards for the type of facility covered by this lease. The FAA Facility Security Management Program defines facility security accreditation standard levels.  The security requirements identified below are tailored specifically for the type of facility covered by this solicitation.  The Lessor shall provide or make accommodation to provide for all the security requirements listed herein for the leased premises covered by this lease agreement:

Contact your local Servicing Security Element (SSE) at       for a list of your security requirements.

The local SSE will determine any additional security upgrades that are required to meet accreditation and shall conduct a final security assessment of the building.  The Lessor shall provide maintenance services to the security upgrades installed within the leased premises and covered under this lease.

E2-Contractor Personnel Suitability Requirements (4/09)

(a) This clause applies to the extent that this contract requires contractor employees, subcontractors, or consultants to have unescorted access to FAA:

(1) Facilities;
(2) Sensitive information; and/or;
(3) Resources regardless of the location where such access occurs, and none of the exceptions of FAA Order 1600.72A, Contractor and Industrial Security Program, Chapter 5, paragraphs 4, 6, 7 and 8 pertains.
Definitions of applicable terminology are contained in the corresponding guidance and FAA Order 1600.72A, appendix A.

(b) Consistent with FAA Order 1600.72A, the FAA Servicing Security Element (SSE) has approved designated risk levels for the positions under the contract. Those designated risk levels are:
[To be entered by the CO based on the 1600-77(s) approved by the SSE]

(c) If a National Agency Check with Inquiries (NACI) or other investigation is required under paragraph (b) for a given position, the contractor will submit to the Contracting Officer (CO) a point of contact (POC) that will enter applicant data into the Vendor Applicant Process (VAP) system (vap.faa.gov). VAP is a FAA system used to process and manage security information for FAA contractor personnel. Each contract may have up to 5 POCs. Once designated, a VAP administrator will provide each POC a Web ID and password.
The type of investigation conducted will be determined by the position risk level designation for all duties, functions, and/or tasks performed and will serve as the basis for granting a favorable employment suitability authorization as described in FAA Order 1600.72A. If an employee has had a previous U. S. Government conducted background investigation which meets the requirements of Chapter 5 of FAA Order 1600.72A and Homeland Security Presidential Directive 12 (HSPD-12), it will be accepted by the FAA. However, the FAA reserves the right to conduct further investigations, if necessary. The contract may include positions that are temporary, seasonal, or under escort only. In such cases, a FAA Form 1600-77 for each specific position will be established as the investigative requirements may differ from the NACI.

The following information must be entered into VAP by the POC for each applicant requiring an investigation:

- Name;

- Date and place of birth (city and state);

- Social Security Number (SSN);

- Position and office location;

- Contract number;

- Current e-mail address and telephone number (personal or work); and

- Any known information regarding current security clearance or previous investigations (e.g. the name of the investigating entity, type of background investigation conducted, contract number, labor category (Position), and approximate date the previous background investigation was completed).

If a prior investigation exists and there has not been a 2 year break in service by the applicant, the SSE will notify the contractor that no investigation is required and that final suitability is approved.

If no previous investigation exists, the SSE will send the applicant an e-mail (this step may be delegated to VAP POC):

- Stating that no previous investigation exists and the applicant must complete a form through the Electronic Questionnaires for Investigations Processing (eQIP) system

- Instructing the applicant how to enter and complete the eQIP form;

- Providing where to send/fax signature and release pages and other applicable forms; and

- Providing instructions regarding fingerprinting.

The applicant must complete the eQIP form and submit other required material within 15 days of receiving the e-mail from the SSE.

For items to be submitted outside eQIP, the contractor must submit the required information with a transmittal letter referencing the contract number to:

Headquarters Contracts:
Manager, Personnel Security Division, AIN-400
800 Independence Avenue, S.W., Room 315
Washington, D.C. 20591

Regional and Center Contracts:

<RECO insert appropriate Regional or Center information here or enter "none" if not applicable>

The transmittal letter must also include a list of all of the names of contractor employees and their positions for which completed forms will be submitted to the SSE pursuant to this Clause.

(d) The contractor must submit the information required by paragraph (c) of this Clause for any new employee not listed in the Contractor's initial submission who is hired into any position identified in paragraph (b) of this Clause.

(e) The CO will provide notice to the contractor when any contractor employee is found to be unsuitable or otherwise objectionable, or whose conduct appears contrary to the public interest, or inconsistent with the best interest of national security. The contractor must take appropriate action, including the removal of such employee from working on this FAA contract, at their own expense. Once action has been taken, the contractor will report the action to the CO and SSE.

(f) No contractor employee will work in a high, moderate, or low risk position unless the SSE has received all forms necessary to conduct any required investigation and has authorized the contractor employee to begin work.

(g) The contractor must notify the CO within one (1) business day after any employee identified pursuant to paragraph (c) of this Clause is terminated from performance on the contract. This notification must be done utilizing the Removal Entry Screen of VAP. If FAA issued the terminated employee and identification card, the contractor must collect the card and submit it to the SSE.

(h) The CO may also, after coordination with the SSE and other security specialists, require contractor employees to submit any other security information (including additional fingerprinting) deemed reasonably necessary to protect the interests of the FAA. In this event, the contractor must provide, or cause each of its employees to provide, such security information to the SSE, and the same transmittal letter requirements of paragraph (c) of this Clause applies.

(i) The contractor and/or subcontractor(s) must contact the Servicing Security Elements (Regional and/or Center Security Divisions) or AIN-400 at Headquarters within one (1) business day in the event an employee is arrested (detained by law enforcement for any offenses, other than minor traffic offenses) or is involved in theft of government property or the contractor becomes aware of any information that may raise a question about the suitability of a contractor employee.

(j) Failure to submit information required by this clause within the time required may be determined by the CO a material breach of the contract.

(k) If subsequent to the effective date of this contract, the security classification or security requirements under this contract are changed by the Government and if the changes cause an increase or decrease in direct contract costs or otherwise affect any other term or condition of this contract, the contract will be subject to an equitable adjustment.

(l) The contractor agrees to insert terms that conform substantially to the language of this clause, including paragraph (k) but excluding any reference to the Changes clause of this contract, in all subcontracts under this contract that involve access and where the exceptions under Chapter 5, FAA Order 1600.72A do not apply.

(m) Contractor employees who have not undergone a background investigation must be escorted at all times. In some instances, a contractor employee may be required to serve as an escort. To serve as an escort, a contractor employee must have a favorably adjudicated fingerprint check and initiated a NACI with FAA.

VI. SECTION F - SPECIAL REQUIREMENTS <insert special requirements - can paste from separate word document>

F1-SPECIAL POWER

F2-OTHER (SPECIFY)

F3-PAINTING FREQUENCY IN PUBLIC AREAS

VII. CERTIFICATION FORMS (8/02) -

See attached forms:
Certification of Seismic Compliance
FAA Safety and Environmental Certification Checklist
Vendor/Miscellaneous Payment Information Form